PROGRAMMERS MANUAL

This document contains information needed to write interface code for the Aprilaire Model 8870 Communicating Thermostat.  For wiring and thermostat set up information refer to the System Installation Manual (RPC part no. 10005754).

NETWORK COMMUNICATION

Network communication is non-isolated, full duplex RS-485 using 4 + 1 wires.  The ‘A’ terminals are the transmit pair while the ‘B’ terminals are the receive pair.  This nomenclature uses the host computer as the reference, so transmit refers to the lines on which the host transmits data to the thermostat while receive refers to the lines on which the host receives data from the thermostat.  The baud rate is selectable between 9600 and 19200.

ASCII based firmware, which is fully compatible with the StatNet command set (revision 1B), is defined below.  Up to 64 uniquely addressed devices are allowed on the network.

There are three response mechanisms depending on the nature of the command request.

- Explicit Address Commands

- Global Address Commands

- Unsolicited Responses

Explicit Address Commands

Explicit Address Commands are those commands that specify a single, particular address in the command header (i.e. SN13 MODE=OFF).  As this command is transmitted down the RS-485 bus, each device connected will receive it into their buffer.  The command will begin to be interpreted by each device.  Once the address is scanned, the entire command will be discarded if it is not that unit’s address.  The unit that WAS explicitly addressed will complete the interpretation of the command, act on it, and respond back to the host.  The command carriage return initiates processing.  Command processing can take up to 265 milliseconds.  Commands that interact with volatile memory take less time to process than those that interact with non-volatile memory.  Responses from an explicitly addressed command can begin immediately after processing, which is as quickly as 20 milliseconds after the command was sent, and not later than 330 milliseconds.

Global Address Commands

Global Address commands are those commands that do not specify any address in the command header (i.e. SN T?).  As with the Explicitly Addressed Commands described above, as this command is transmitted, each device connected will receive it into their buffer.  Since there is no address, the units will recognize this as a global command. Each unit will complete the interpretation of the command, act on it, and respond back to the host.   However, unlike the Explicit commands where only one unit will be responding, global commands imply that each unit will be responding.  Therefore the responses from global commands must be scheduled to prevent collisions over the communications channel.  Each device waits for its turn to issue its response.  The order of the response coincides with the unit address.   Therefore the thermostat with address #1 will respond first, then #2, #3, on up to #64.

Responses from a global command can begin as quickly as 20 milliseconds after the command was sent.  The actual time lapse for the first response is dependent on the lowest addressed device on the thermostat network.  If there was no address #1 on the network, then the first response opportunity will be idle; simply passing time until the next response opportunity.  Of course, if there is no address #2 either, then there will be a delay as this opportunity passes.   If no response begins within X*265 milliseconds (X is defined as the “Number of Thermostats on the Network” which is configurable in Thermostat Set Up), then one or more of the units did not

understand the command, the unit is in QUIET or SILENT mode, or is off-line.   The last unit to respond will be the unit with the highest address on the channel.  Since the highest allowed address is 64, the longest delay time for the start of the last response is approximately 17 seconds.

Do not skip addresses unless absolutely necessary to avoid unwanted delays in responses.

Unsolicited Responses

Change-Of-State (COS) responses are sent whenever a COS is detected, for a condition specified in the COS commands, when the COS has been turned “ON”.  There are twelve COS commands described in detail in the Command Set portion of this document.  Change of State responses are sent so that a host computer connected to the thermostat network need not poll in order to see if any thermostat variable change has taken place.

In unsolicited responses, no actual command has been sent down to solicit the response (once the COS commands are sent, the unit will automatically respond on a change of state).  Unsolicited responses are scheduled, according to address, in a manner similar to global responses. Each device waits for its opportunity to come up, and issues its response at that time.

Unsolicited responses can begin as quickly as 20 milliseconds after the COS was detected.  As with global responses, unsolicited responses are issued only during the units assigned opportunity to respond. COS responses will be received from a specific device no later than X*265 milliseconds (X is defined as the “Number of Thermostats on the Network” which is configurable in Thermostat Set Up), since the unit will only respond in its unique opportunity.

Since the signal used to synchronize every device is the <CR> terminator of a command, the host must issue a <CR> every 12 hours.  Note that any command, appended with a carriage return, sent down the communications link from the host qualifies as a synchronizing transmission.

## Command Transmission Timing

To prevent missed commands or prevent causing communication collisions adhere to the following rules when sending commands to thermostats:

- When no response is to be received, allow no less than 265 milliseconds after issuing a command (explicit or global) before issuing a second command to the same thermostat (i.e. CR=QUIET or CR=SILENT).  This allows sufficient time for processing regardless of the command.

- When a response to an explicit command is desired, allow no less than 330 milliseconds after issuing an explicit (specifically addressed) command before issuing a second command to the same thermostat (i.e. CR=NORMAL).

- There can be a difference between the programmed time delay and actual time delay depending on the software/hardware used, so you may want to allow for some variation.

- Explicit queries (requests for information), except NAME?, ID?, PMES1? PMES2?, PMES3 and  PMES4?, can be sent with 20 milliseconds between commands.

- Commands that change the status of a variable generally require 330 milliseconds.  The exceptions are CR, C1 – C12 and FAN which require only 20 milliseconds.

- When a response to a global command is desired, allow no less than (265 * “No. of Thermostats on the Network”) milliseconds after issuing a global command before issuing a second command when a response is desired (i.e. CR=NORMAL).  Round up to the nearest second.  The default value for “No. of Thermostats on the Network” is 32, so if unchanged allow 9 seconds between commands.

Rounding up will allow for some variation between programmed time delay and actual time delay.  Some experimentation may be required to ensure the minimum time between commands is respected.

To maximize communication speed consider the following:

- Communicate at 19200 baud

- Do not skip addresses on the thermostat network unless absolutely necessary.

- Set the “Number of Thermostats on the Network” to the highest addressed thermostat.  If you have only six thermostats address them 1 through 6 and set the highest address to six.

- Only turn on the necessary change of state variables (COS – refer to the command descriptions).

- Unless a response is required, when sending a large number of commands, set the Command Response to Quiet or Silent.  If responses are needed, it may be faster to explicitly query each thermostat on the network.

##### NETWORK OVERRIDE or HOLD

Invoking Network Override causes the thermostat to disregard all received commands except requests for data.  This means that no response to action commands will be forthcoming.  Network Override can be invoked at the thermostat (by using the Enter button) or through the command set (SN HOLD=ON).  Unsolicited data transmission is unaffected.  Should the thermostat be receiving communication when Network Override is invoked, network override will begin following the reaction caused by the received communication.

If receiving no response to a command will cause disruption to your program, then there are two options: disable this feature or begin every command transmission by “SN HOLD=OFF”.  To disable the feature, ensure that Hold is “OFF” at each thermostat and send the command “SN NETLK=1”.  Alternatively it could be disabled through the Thermostat Set Up menu.

How to Detect When a Thermostat Has Gone Off-line

When a thermostat goes off-line (reinitializes) the Change of State (COS) variables return to default values - OFF.  The consequence of this occurring is that unsolicited responses will not be sent by the thermostat (i.e. the automation system will not know when something has been changed at the thermostat).  There are two reasons that a thermostat will have gone off-line: the power had been removed and reinstated or the Thermostat Set Up menu has been entered.  When this occurs the COS variables must be reset.  It is good practice to periodically check (once every 15 minutes is a good start) that all thermostats are still responding.  Simply query one of the COS variables you have turned on to verify it is still on.  For example periodically send the command “SN C2?”.  You should receive the response “SNx C2=ON”; where x is the address of each thermostat on the network.

# Command set Syntax

Upper or lower case letters may be used for all commands.  Invalid characters will immediately invalidate a command, so the use of backspace or delete is not allowed (applies mainly when interacting with the thermostat using HyperTerminal).

All Model 8870 commands will begin with the characters SN.  Immediately following the SN, without any intervening spaces (blanks), will be the address (#) from 1 to 64 of the Model 8870 Thermostat with which you are communicating.  Single digit addresses may be sent as a two digit address with a leading zero.  Omitting the address, or using a 0 (zero) in place of a space makes the command global, and all connected thermostats will respond. Following this initial command sequence, spaces may be inserted at this point only, for clarity between commands.  The next portion is the command or variable [Command].  The table below describes the available commands.  The next portion[? Or =] is the action to be performed: ? corresponds to “state your value”, = corresponds to “set your value”.   Spaces are allowed between the command and the action.  The final portion, [Value], is used only if a command or variable is to be set.  The value must follow the action with no intervening spaces.  A carriage-return ( Enter	 is used as the terminator for the command string.   Line feeds (LF) should not be sent with commands as this is a recognized ASCII character and invalidates any command received between the line feed and the next carriage return.

EXCEPTIONS: The command SN? or SN0? will respond with all connected thermostats returning their address.  The command BLTON performs its intended action without the need for a value.

# Command Response Syntax

Model 8870 will respond by supplying the information requested or by confirming the completion of an action command.  The response syntax is generally the same as that used for commands, but no spaces separate command, action or value.  Responses are sent in upper case  ASCII format.  Details of the response can be found in the detailed description section for each command.  Should a command not be recognized, no response will be forthcoming – there is no ERROR message.

All of the commands are summarized in the following list.  A detailed description of each command follows the table.  Unless otherwise noted as “Read Only” or “Write Only”, all commands are “Read and Write”.

| Command | Description | Value |
| --- | --- | --- |
| Communication Control Commands |
| CR | Command Response Control | Silent / Quiet / Normal |
| C1 | Change of State (COS) – HVAC relays | ON/OFF |
| C2 | COS – Temperature | ON/OFF |
| C3 | COS – Remote Temperature | ON/OFF |
| C4 | COS – Contact Closures | ON/OFF |
| C5 | COS – Set Points | ON/OFF |
| C6 | COS – Network Override | ON/OFF |
| C7 | COS – Mode | ON/OFF |
| C8 | COS – Fan | ON/OFF |
| C9 | COS – Scroll Up activation | ON/OFF |
| C10 | COS – Scroll Down activation | ON/OFF |
| C11 | COS – Enter Button activation | ON/OFF |
| C12 | COS – Backlight Ready | ON/OFF |
| CP | Command Configuration Pattern | 1 / 2 |
| HOLD | User Hold Status | ON / OFF |
| NAME | Location Name | <String> |
| ID | Report Model No. and software rev. | Read Only |
| Thermostat Sensing Commands |
| SCALE | Command Temperature Scale | F / C (Faherenheit/Celcius) |
| CT | Controller Type; Temperature or Humidity. Set to Humidity only when auxiliary humidity control sensor is detected. 0 = Temperature controller, 1 = Humidity controller | Read Only |
| TEMP, T | Report Thermostat Room Temperature | Read Only |
| HUM | Report Thermostat Room Humidity | Read Only |
| RSM | Identify all external sensors connected to a thermostat’s local communication network | Read Only |
| RxSy (x = 1-4; y = 1,2) | Report value of any sensor on thermostat’s local communication network | Read Only |
| OT | Report Thermostat Remote “Outdoor” Temperature | Read Only |
| R | Report Thermostat Remote “Outdoor” Temperature | Read Only |
| OH | Report Thermostat Remote Humidity | Read Only |
| Thermostat HVAC Operational Commands |
| SH | Heat Mode Set Point | Two or three digit integer: 40 – 88 for °F; 4 – 31 for °C |
| SH++ | Increment heat set point | Integer value which when added to the current heat set point does not fall outside the SH limits |
| SH-- | Decrement heat set point | Integer value which when deducted from the current heat set point does not fall outside the SH limits |
| SC | Cool Mode Set Point | Two or three digit integer: 42 – 90 for °F; 6 – 33 for °C |
| SC++ | Increment cool setpoint | Integer value which when added to the current cool set point does not fall outside the SC limits |
| SC-- | Decrement cool setpoint | Integer value which when deducted from the current cool set point does not fall outside the SC limits |
| S | Current Mode Set Point | Two or three digit integer (see next two commands) |
| SP++ | Increment current mode set point | Integer value which when added to the current mode set point does not fall outside the SH and SC limits |
| SP-- | Decrement active setpoint | Integer value which when deducted from the current mode set point does not fall outside the SH and SC limits |
| DIF1 | Temperature control differential for first stage heat/cool. | 0.5° – 2° in 0.5° increments |
| DIF2 | Temperature control differential for second stage heat/cool. | 0.5° – 2° in 0.5° increments |
| OFFSET | Amount to offset the display temperature from the sensed temperature. | ±3°, 1° increments |
| SHUM | Humidify Mode setpoint | Integer, 2 or 3 digit, value 10-90 |
| SHUM++ | Increment humidify setpoint | Integer value which when added to the current humidify set point does not fall outside the SHUM limits |
| SHUM-- | Decrement humidify setpoint | Integer value which when deducted from the current humidify set point does not fall outside the SHUM limits |
| SDEH | Dehumidify Mode setpoint | Integer, 2 or 3 digit, value 10-90 |
| SDEH++ | Increment dehumidify setpoint | Integer value which when added to the current dehumidify set point does not fall outside the SDEH limits |
| SDEH-- | Decrement dehumidify setpoint | Integer value which when deducted from the current dehumidify set point does not fall outside the SDEH limits |
| MODE,M | Thermostat Mode of Operation | A / C / H / E / OFF (Auto/Cool/Heat/EMHT/Off) Humid/Dehum when operating as a humidity controller |
| FAN, F | Fan Switch Setting | A / ON (Auto/On) |
| HVAC, H | Report HVAC Relay States | Read Only |
| HiBP | Temperature value above which W1 terminal is locked out (heat pump equipment configuration only) | 40° - 80°, 5° increments |
| LoBP | Temperature value below which compressor terminals are locked out (heat pump equipment configuration only). | 0° - 40°, 5° increments |
| Text Messaging Commands |
| DATE | Thermostat date value | MMDDYY |
| TIME | Thermostat time value | HHMM |
| PMES1 | First message in the permanent message sequence | 32 character text string |
| PMES2 | Second message in the permanent message sequence | 32 character text string |
| PMES3 | Third message in the permanent message sequence | 32 character text string |
| PMES4 | Fourth message in the permanent message sequence | 32 character text string |
| TMPMES | Temporary message | 32 character text string |
| MENU | Operates the text messaging display in a User-Interactive mode. MSG is used to display messages when MENU is on. | ON/OFF |
| MSG | User-Interactive message | 32 character text string |
| Keypad Lockout Commands |
| FanLK | Determines the degree to which the user is locked out of fan control. | 0=no lockout, 1=time limited change, 2=total lockout |
| ModeLK | Determines the degree to which the user is locked out of mode control. | 0=no lockout, 1=time limited change, 2=total lockout |
| NetLK | Determines the degree to which the user is locked out of network override control. | 0=no lockout, 1=total lockout |
| Updnlk | Determines the degree to which the user is locked out of increment/decrement control. | 0=no lockout, 1=time limited change, 2=time and value limited change, 3=total lockout |
| LKTime | Time value (minutes) that an input change is allowed until it reverts back to the pre-change value. | Integer value between 0 and 255 |
| LKLimit | Number limit that the increment/decrement is allowed to change when locked. | Integer value between 0 and 20 |
| Monitoring Module Commands |
| CC | Digital Input States | All of these commands will simply return a response – no action at the thermostat occurs. If inquired all will respond as though all inputs/outputs/led’s are OFF. |
| CO | Digital Output States |  |
| Ln (n = 1 to 4) | Comm. Card LED Light 1,2,3 or 4 |  |
| Auxiliary Information Commands |
| EQUIPCONFIG | Reports the setting of the thermostat configuration dip switches | Read Only |
| BLREADY | Reports ready state of photosensor | 0 = Backlight not in ready state, 1 = Backlight in ready state. |
| BLTRIG | Sets relative room light intensity level required to put backlight in ready state | 0 = darker, 1=lighter |
| BLTON | Turns on backlighting, regardless of ready state, for 10 seconds. | No Value Required for this Command |
| ENTR | Enter button status | 1 = State change from inactive to active, 0 = State change from active to inactive |
| SCUP | Scroll Up button status | 1 = State change from inactive to active, 0 = State change from active to inactive |
| SCDN | Scroll Down button status | 1 = State change from inactive to active, 0 = State change from active to inactive |

# The following command descriptions describe the use of the command when setting a particular variable.  Inquiries can be made with all commands (with the exception of the SCUP, SCDN, BLTON and ENTR commands) to determine the existing value of a variable.  Inquiry is done using the following syntax:

# SN [address number, or <blank> or 0 (zero) for global] “COMMAND” ?; where command is the variable whose value is desired.

# Communication Control Commands

These commands control how Model 8870 will communicate.

CR	COMMAND RESPONSE CONTROL

Model 8870 normally responds to all commands.  All responses begin with the string SNx where x is the Model 8870 network address number. (Note the address range is from 1 to 64.)  All responses are concluded with a carriage return.  The Command Response Control command allows you to change the response actions.

SILENT mode will not reply to any command.  Action commands (telling Model 8870 to change a setting) will be acted upon, but no response will be returned indicating that the action was performed.  All inquiry commands (asking Model 8870 for information) will be ignored.  COS commands will be received by Model 8870, but Model 8870 will not act upon those commands while in the silent mode.

Command Format: SN[address number or <blank> for global] CR=S or SILENT

Reply Format: No response will be received.

NORMAL mode will set Model 8870 to the default mode where a response is always given.  This is the default setting.

Command Format: SN[address number or <blank> for global] CR= N or NORMAL

Reply Format: SN[address number] CR=NORMAL

QUIET mode will not reply to action commands.  Inquiry commands will be responded to.  This suppresses the feedback response on action commands.  COS commands will be heard and carried out.

Command Format: SN[address number or <blank> for global] CR= Q or QUIET

Reply Format: No response will be received.

C1 – C12	CHANGE-OF-STATE NOTIFY COMMAND

Command Format: SN[address number or <blank> for global] C1 through C12=ON or OFF

Reply Format: SN[address number] C1 through C12=ON or OFF

Model 8870 can be configured to send out a message upon a Change-Of-State (COS) for any of the variables below.  Simply turn on the COS flag for any of the variables for which the automation system needs to be kept informed.  In this way, a computer connected to Model 8870 need not poll in order to see if anything has occurred – it can simply ignore Model 8870 until it hears from it.  The computer will only be notified if some event takes place at the thermostat unit.  If all COS flags are set to OFF, the Model 8870 will not report anything automatically, and the computer unit must send inquiries to Model 8870 to determine any new conditions.  (This equates to a ‘polling’ mode, whereas with any COS flag ON equates to an interrupt mode.)  There are twelve COS indicators, which by default, are set OFF on power-up or reset.  Refer to the section describing each individual command for details on the responses.

| C1 | HVAC Control Circuits | When any thermostat output goes from an energized state to a de-energized state or vice versa. Example of response: SN1 HVAC = G+Y1+W1-Y2-W2-B-O+ |
| --- | --- | --- |
| C2 | Temperature or Humidity | When the thermostat room temperature (or humidity) reading changes. Examples of response: SN3 T = 72F, SN6 HUM = 36% |
| C3 | Remote Temperature or Humidity | When the thermostat remote temperature (or humidity) reading changes. Examples of response: SN15 OT = 86F, SN4 OH = 57% |

| C4 | Contact Closures | Applies to Monitoring Module output status. To be finished when design specifications have been finalized. |
| --- | --- | --- |
| C5 | Thermostat Set Points | When the thermostat Heat, Cool, Humidify or Dehumidify temperature setting is changed by use of the up and down buttons on the thermostat. Examples of response: SN1 SH = 68F, SN5 SC = 78F, SN13 SHUM = 32%, SN4 SDEH = 65% |
| C6 | Network Override (Hold) Function | When thermostat network control has been overridden or returned at the thermostat. Example of response: SN1 HOLD = ON |
| C7 | Thermostat Mode | When the mode of operation (i.e. Heat, Cool, Auto, Off or Emergency Heat) has been changed by use of the thermostat Mode button. Example of response: SN3 M = AUTO |
| C8 | Thermostat Fan State | When the fan is changed to On or Auto by use of the thermostat Fan button. Example of response: SN2 F = AUTO |
| C9 | Scroll Up (thermostat button) | When the scroll-up button (top button next to the text messaging display) is pressed or released. Example of response: SN4 SCUP = ON, SN4 SCUP = OFF |
| C10 | Scroll Down (thermostat button) | When the scroll-down button (bottom button next to the text messaging display) is pressed or released. Example of response: SN5 SCDN = ON, SN5 SCDN = OFF |
| C11 | Enter | When the ENTER button is pressed or released. Example of response: SN3 ENTR = ON, SN3 ENTR = OFF |
| C12 | Backlight Ready | When the thermostat backlight enters the ready state (i.e. room illuminance less than that set at the thermostat). Example of response: SN1 BLREADY = ON |

CP	COMMAND CONFIGURATION PATTERN

# Command Reply Format: SN[address number or <blank> for global] CP=1 or 2

Reply Format: SN[address number] CP=1 or 2; No response sent when set to CP=1 (i.e. no response to SN1 CP=1)

Model 8870 can retain two independent sets of communication configuration settings.  Each set contains the state of all Change-Of-State (COS) settings and the Command Response (CR) setting.  Default values for CP #1 and CP #2 are shown below.  IMPORTANT: Once a configuration pattern has been selected, any changes you make to the communications control commands are assigned to the active configuration pattern.  By default, CP #1 is active upon startup.  The benefit of this command is to facilitate having a standard configuration for normal operation and a second configuration for special functions.  CP #2 is convenient for those who wish to integrate the text messaging display into their automation system.  You may alternate between these two configurations by simply sending the Configuration Pattern command.

| DEFAULT SETTINGS FOR CONFIGURATION PATTERN 1 | DEFAULT SETTINGS FOR CONFIGURATION PATTERN 2 |
| --- | --- |
| CR | NORMAL | CR | NORMAL |
| C1 | OFF | C1 | OFF |
| C2 | OFF | C2 | OFF |
| C3 | OFF | C3 | OFF |
| C4 | OFF | C4 | OFF |
| C5 | OFF | C5 | OFF |
| C6 | OFF | C6 | OFF |
| C7 | OFF | C7 | OFF |
| C8 | OFF | C8 | OFF |
| C9 | OFF | C9 | ON |
| C10 | OFF | C10 | ON |
| C11 | OFF | C11 | ON |
| C12 | OFF | C12 | OFF |

HOLD		NETWORK OVERRIDE

Command Format: SN[address number or <blank> for global] HOLD=ON or OFF

Reply Format: SN[address number] HOLD=ON or OFF

Model 8870 incorporates an ENTER button.  This button has three functions: user interactive Thermostat Set-Up, User Reset Message resetting and network override.  During Thermostat Set-Up the user interacts with the text messaging display to select various operational parameters and this button is used to enter those selections.  When the thermostat receives a User Reset Message command this button is used clear the message from the text messaging display.  During all other times, this button is used to override network control of the thermostat: temperature changes, mode changes and fan state changes are controlled only by the buttons on the thermostat.  This command can be used to change the Network Override status or HOLD status regardless of what the text messaging display is doing.  When activated (HOLD = ON), “NETWORK OVERRIDE” shows on the segmented display of the thermostat.  The NETLK command enables or disables this feature.

NAME		LOCATION NAME

Command Format: SN[address number or <blank> for global] NAME={text string, 16 characters or less – no spaces allowed}

Reply Format: SN[address number]{NAME}

You can have Model 8870 append an identifier name to its address when it transmits a message.  The identifier string must be 16 characters or less.

An example sequence is: (NOTE: commands are bold, responses are shown in Italics and <CR> represents a carriage return)

SN1 NAME=MASTER BEDROOM<CR>	Set a name to the thermostat with address #1

SN1MASTER BEDROOM	Model 8870 confirms that a new name is assigned

SN1 T?<CR>	Inquire temperature at thermostat #1

SN1MASTER BEDROOM T=72F	Model 8870 responds with the temperature at thermostat #1, now called Master Bedroom

SN1 NAME=<CR>	Clear the name of the thermostat with address #1

SN1	Model 8870 confirms that the name has been removed

ID	REPORT THERMOSTAT MODEL NUMBER and SOFTWARE REVISION

Command Format: SN[address number or <blank> for global] ID?

Reply Format: SN[address number] MODEL#  8870 REV: x.x RPC 2001; where x.x represent the current firmware revision level.

Model 8870 will respond with the model number followed by the current software revision.

# Thermostat Sensing Commands

These commands are used to inquire and set scale for the various temperature or humidity values read by the thermostat.

SCALE		SET TEMPERATURE SCALE

Command Format: SN[address number or <blank> for global] SCALE=F or C

Reply Format: SN[address number] SCALE=F or C

Thermostat temperature readings can be displayed and communicated in either Celsius (Centigrade) or Fahrenheit as dictated by this command.  The setting at initial power up will default to °F.  Subsequent start-ups (i.e. loss of power or resets) will default to the scale that was last set.  Scale setting applies to the room temperature, the remote temperature and all temperature settings.  When a temperature setting is to be communicated to the thermostat, and no scale is designated, the temperature will be read using the scale that has been set for the thermostat.

CT	CONTROLLER TYPE

Command Format: SN[address number or <blank> for global] CT?

Reply Format: SN[address number] CT=0 (temperature controller) or 1 (humidity controller)

Connecting an optional support module, configured for humidity control, to Model 8870 changes it from a temperature controller to a humidity controller.  Controller type is a read-only command.  This command is used to determine which Model 8870 thermostats connected to the network are currently acting as temperature controllers or humidity controllers.  The response designations are CT=0, for temperature controller or CT=1, for humidity controller.

TEMP		THERMOSTAT TEMPERATURE

Verbose Command Format: SN[address number or <blank> for global] TEMP?

Short Command Format: SN[address number or <blank> for global] T?

Reply Format: SN[address number] T={value}F or {value}C

Thermostat temperature is that shown on the display of the thermostat and against which the temperature settings are compared for control purposes.  This temperature can be from the thermostat’s on-board temperature sensing element or from attached support module(s) configured for temperature control.  Model 8870 responds with the temperature in the scale set by the SCALE command.  It appends a C or F to the value for clarity.

# HUM		THERMOSTAT HUMIDITY

Command Format: SN[address number or <blank> for global] HUM?

Reply Format: SN[address number] H={value}%

Connecting an optional support module, configured for humidity control, to Model 8870 changes it from a temperature controller to a humidity controller.  Thermostat humidity is that shown on the display of the thermostat and against which the humidity settings are compared for control purposes.  This humidity reading is that measured attached support module(s) configured for humidity control.  Model 8870 responds with the humidity reading appended by a “%” for clarity.

RSM		REMOTE SENSOR MODULES

Command Format: SN[address number or <blank> for global] RSM?

Reply Format: SN[address number] RSM= M1:S1,S2 M2: S1,S2 M3: S1,S2 M4: S1,S2	If there is no support module at a module address then it will not be shown.  S1,S2 show what type of sensor is connected as sensor #1 and Sensor #2 respectively.  Sensor (S1, S2) options include:

CT	Control temperature sensor (i.e. replaces control value of thermostat)

RT	Remote temperature sensor (i.e. for display only)

CH	Control humidity sensor

RH	Remote humidity sensor

XX	No sensor attached at this position

Up to four addressable support-modules can be connected to a thermostat’s local communication network.  Two sensors can be connected to each support module, each can be a temperature sensor or a humidity sensors depending on the support module model.  Each sensor can be individually configured as control sensors or remote sensors (for display only).  This command returns the number of support modules connected to a thermostat, what type of sensors are attached to them and how those sensors are configured.  The response is made up of the number of modules (Mx) and the type of each of the two sensors connected to that module (RT, CT, RH, CH or XX).  The first sensor listed is considered sensor #1 for that module and the second listed is considered sensor #2.  Following is an example that illustrates the response (commands are bold responses are shown in italics):

SN1 RSM?	Request information about sensors connected to thermostat with address #1

SN1 RSM= M1:RT,RT M2:CT,CT M3:RH,CT	Model 8870 responds that there are three support modules attached to thermostat 1, that there are two remote temperature sensors on the module with address #1, two control temperature sensors on the module with address #2 and that the module with address #3 has a remote humidity sensor as sensor #1 and a control temperature sensor as sensor #2.

RxSy	REMOTE SENSOR VALUE

Command Format: SN[address number or <blank> for global] RxSy?; where x is the support module address (1 - 4) and y is the sensor number (1 or 2)

Reply Format: SN[address number] RxSy={value}F, C or %; where x is the support module address (1 - 4) and y is the sensor number (1 or 2)

Up to four addressable support-modules can be connected to a thermostat’s local communication network (LCN).  Two sensors can be connected to each support module.  This value is used to retrieve the value of the sensor in the appropriate units of measure.  The ‘RSM’ command is used to determine what sensors of what type are available on the thermostat LCN.

OT	THERMOSTAT REMOTE “OUTDOOR” TEMERATURE

Command Format: SN[address number or <blank> for global] OT?

Reply Format: SN[address number] OT={value}F or C

Alternate Command Format: SN[address number or <blank> for global] R?

Alternate Reply Format: SN[address number] R={value}F or C

Up to four addressable support-modules can be connected to a thermostat’s local communication network.  Two sensors can be connected to each support module, each can be a temperature sensor or a humidity sensors depending on the support module model.  Each sensor can be individually configured as control sensors or remote sensors (for display only).  Sensor #1, configured to be “remote”, of the support module with address #1 is the source for remote outdoor temperature. Model 8870 responds with the temperature in the scale defined by the SCALE command and appends a C or F to the value for clarity.  Should no sensor be attached the value will show “- -“.  This is the temperature value shown on the lower left of the thermostat display and is the value used for high and low balance point control (for heat pump use only).

The alternate command and reply formats have been implemented to maintain backward compatibility with earlier thermostat versions.

OH	THERMOSTAT REMOTE “OUTDOOR” HUMIDITY

Command Format: SN[address number or <blank> for global] OH?

Reply Format: SN[address number] OH={value}%

Up to four addressable support-modules can be connected to a thermostat’s local communication network.  Two sensors can be connected to each support module; each can be a temperature sensor or a humidity sensor depending on the support module model.  Each sensor can be individually configured as control sensors or remote sensors (for display only). The humidity sensor configured to be “remote” of the support module with address #1 is the source of remote humidity. Model 8870 responds with the humidity value appended by a “%” for clarity.  Should no sensor be attached the value will show “- -“.  This is the humidity value shown on the lower left of the thermostat display.

Thermostat HVAC Operational Commands

These commands are used for temperature control and other thermostat operational parameters.

SH	TEMPERATURE SETTING – HEAT

Command Format: SN[address number or <blank> for global] SH={value}; One through three digit integer value between 40 and 88 if scale set to °F or between 4 and 31 if scale set to °C.

Reply Format: SN[address number] SH={value}F or C depending on set temperature scale

The heat setting is the temperature setting against which the current room temperature is compared to control the heating outputs of the thermostat.  The value is assumed to be in the temperature scale set using the SCALE command.  If the integer value is outside the allowable range for the set temperature scale the command will be ignored.

# SH++/SH --	INCREMENT OR DECREMENT TEMPERATURE SETTING – HEAT

Command Format: SN[address number or <blank> for global] SH++ or SH--=Integer value (°F or °C designation not required)

Reply Format: SN[address number] SH++ or SH--=Integer value F or C

These commands are used to raise (SH++) or lower the (SH--) the heat temperature setting by a specified value.  The value is assumed to be in the temperature scale set using the SCALE command and the response will include a scale designator.  Should the resultant change be outside the allowable range for the set temperature scale, the command will be ignored.

# SC	TEMPERATURE SETTING – COOL

Command Format: SN[address number or <blank> for global] SC={value}; One through three digit integer value between 42 and 90 if scale set to °F or between 6 and 33 if scale set to °C

Reply Format: SN[address number] SC={value}F or C depending on set temperature scale

The cool setting is the temperature setting against which the current room temperature is compared to control the cooling outputs of the thermostat.  The value is assumed to be in the temperature scale set using the SCALE command.

# SC++/SC --	INCREMENT OR DECREMENT TEMPERATURE SETTING – COOL

Command Format: SN[address number or <blank> for global] SC++ or SC--=Integer value

Reply Format: SN[address number] SC++ or SC--=Integer value F or C

These commands are used to raise (SC++) or lower the (SC--) the cool temperature setting by a specified value.  The value is assumed to be in the temperature scale set using the SCALE command and the response will include a scale designator.  Should the resultant change be outside the allowable range for the set temperature scale, the command will be ignored.

# S	CURRENT MODE TEMPERATURE SETTING

Command Format: SN[address number or <blank> for global] S={value}; One through three digit integer value F or C – see Heat and Cool Setting commands for allowable range.

Reply Format: SN[address number] SH={value} or SC={value}; depending on which value was changed.

The Model 8870 thermostat holds two temperature settings in memory, a heat setting and a cool setting.  In the Heat mode of operation, the heat setting is used as the control point and in the Cool mode of operation the cool setting is the control point.  In the Auto mode of operation the thermostat will control the temperature using either the heat setting or the cool setting depending on which the current room temperature is closest.  The Setpoint (S) command is used to change the active temperature setting, so knowledge of the current mode of operation is not required.  If the thermostat is currently in the Heat mode, the heat setting will be changed.  If the thermostat is in the Cool mode the cool setting will be changed.  If the thermostat is in the Auto mode, the temperature setting corresponding to the last HVAC equipment call (i.e. current active reversing valve output).  The thermostat will automatically maintain a two degree (2°) difference between the heating and cooling settings regardless of which mode of operation is currently active, by raising or lowering the value not being adjusted if the two degree separation rule is violated by this command.

# SP++/SP --	INCREMENT OR DECREMENT CURRENT MODE TEMPERATURE SETTING

Command Format: SN[address number or <blank> for global] SP++ or SP--=Integer value F or C

Reply Format: SN[address number] SP++ or SP--=Integer value F or C

These commands are used to raise (SP++) or lower the (SP--) the current mode temperature setting by a specified value. The value is assumed to be in the temperature scale set using the SCALE command and the response will include a scale designator.  Should the resultant change be outside the allowable range for the set temperature scale, the command will be ignored.

DIF1, DIF2, & OFFSET	TEMPERATURE CONTROL CONFIGURATION SETTINGS

Command Format: SN[address number or <blank> for global] DIF1=Integer value between 0 and 3 inclusive

Reply Format: SN[address number] DIF1=Integer value between 0 and 3 inclusive

Command Format: SN[address number or <blank> for global] DIF2 =Integer value between 0 and 3 inclusive

Reply Format: SN[address number] DIF2 =Integer value between 0 and 3 inclusive

Command Format: SN[address number or <blank> for global] OFFSET=Integer value between -3 through +3

Reply Format: SN[address number] OFFSET=Integer value between -3 through +3

Three temperature control variables can be accessed through the Model 8870 command set; they are first stage differential (DIF1), second stage differential (DIF2) and display temperature offset or bias (OFFSET).

Model 8870 is an on/off type temperature controller.  This means that at some temperature below or above the temperature setting the equipment is turned on, generating or extracting heat at 100% capacity, and at some temperature the equipment is turned off.  Differential refers to the deviation from setting that the temperature is allowed to be before the control outputs are turned on or off.

The default differential setting is 0.5° F or C for both DIF1 and DIF2.  Differential settings for each stage can be increased in increments of 0.5°F or C up to 2°F or C.  The SN1 DIF1 command is used to add to the default differential of 0.5° in increments of 0.5°.  For example, SN1 DIF1=1 sets the first stage differential at 1°F or C (= 0.5° + 1*0.5°), while SN1 DIF1=3 sets the first stage differential at 2° F or C (= 0.5° + 3*0.5°) and SN1 DIF1=0 returns the differential to 0.5° F or C.  Second stage differential setting is the value above or below the first stage differential setting that the temperature is allowed to deviate before turning on the second stage of either heating or cooling.  For example, setting SN1 DIF1=0 and SN1 DIF2=2 will result in first stage operation at temperatures above or below 0.5° while second stage will be activated at 0.5° + 1.5° = 2° above or below the setting.

Thermostats are factory set to be accurate to within 1° between 60°F and 80°F.  Temperature comfort however can be a relative condition, so Model 8870 allows the temperature displayed on the thermostat to be artificially offset.  OFFSET is used to offset the display temperature.  For example setting SN1 OFFSET=-3 will change a displayed temperature reading of 72°F to be 69°F.

SHUM		HUMIDIFY CONTROL SETTING

Command Format: SN[address number or <blank> for global] SHUM=Two or three digit integer value between 10 and 90

Reply Format: SN[address number] SHUM={value}%

Connecting an optional support module, configured for humidity control, to Model 8870 changes it from a temperature controller to a humidity controller.  The corresponding modes of operation are Humidify, Dehumidify, Humidify or Dehumidify and Off.  SHUM is used to set the “Humidify” control setting.  The humidify setting is that against which the current room humidity is compared to control the humidify output of the thermostat.

# SHUM++/SHUM - -	INCREMENT OR DECREMENT HUMIDIFY SETTING

Command Format: SN[address number or <blank> for global] SHUM++ or SHUM--=Integer value followed by a %

Reply Format: SN[address number] SHUM++ or SHUM--={value}%

These commands are used to raise (SHUM++) or lower the (SHUM--) the humidify setting by a specified value.  Should the resultant change be out of the allowable humidify setting limits, the command will be ignored.

SDEH		DEHUMIDIFY CONTROL SETTING

Command Format: SN[address number or <blank> for global] SDEH=Two or three digit integer value between 10 and 90 followed by a %

Reply Format: SN[address number] SDEH={value}%

Connecting an optional support module, configured for humidity control, to Model 8870 changes it from a temperature controller to a humidity controller.  The corresponding modes of operation are Humidify, Dehumidify, Humidify or Dehumidify and Off.  SHUM is used to set the “Humidify” control setting.  The dehumidify setting is that against which the current room humidity is compared to control the dehumidify output of the thermostat.

# SDEH++/SDEH - -	INCREMENT OR DECREMENT HUMIDIFY SETTING

Command Format: SN[address number or <blank> for global] SDEH++ or SDEH--=Integer value followed by a %

Reply Format: SN[address number] SDEH++ or SDEH--={value}%

These commands are used to raise (SDEH++) or lower the (SDEH--) the dehumidify setting by a specified value.  Should the resultant change be out of the allowable dehumidify setting limits, the command will be ignored.

# MODE		THERMOSTAT MODE OF OPERATION

Verbose Command Format: SN[address number or <blank> for global] MODE=HEAT, COOL, EMHT, HUMID, DEHUM, AUTO or  OFF (Alternatively H may be used for Heat, C for Cool, A for Auto or E for EMHT)

# Short Command Format: SN[address number or <blank> for global] M= HEAT, COOL, EMHT, HUMID, DEHUM, AUTO or  OFF (Alternatively, H may be used for Heat, C for Cool, A for Auto or E for EMHT)

# Reply Format: SN[address number or <blank> for global] M=HEAT, COOL, E, HUMID, DEHUM, AUTO or OFF

This command dictates what equipment the thermostat will turn on/off to control temperature.  In the HEAT mode, only the heating equipment will be used, in the COOL mode, only the cooling equipment will be used. When the thermostat has been configured to operate a heat pump (this is a dip-switch configuration on the thermostat), Emergency Heat mode is available.  In the Emergency Heat (EMHT) mode, only the back-up heat source is used.

When a humidity control sensor (optional accessory) is wired to the thermostat it becomes a humidity controller instead of a temperature controller.   Operating as a humidity controller, HUMID mode will operate the humidifier only, DEHUM mode operates the dehumidification equipment only.

In the AUTO mode, either the heating or cooling equipment will be used, or if acting as a humidity controller, either the humidification or dehumidification equipment will be used. Care must be exercised in the selection of AUTO mode. The AUTO mode should not be set during extremely high or extremely low outdoor temperature conditions.  Operating the cooling equipment when the outdoor temperature is low (i.e. below 50°F) can be damaging to the equipment as can operating the heating equipment when the outdoor temperature is too high.  Consult with HVAC installers for safe operating conditions.

The OFF mode effects equipment operation only.  When OFF, the thermostat does not control temperature or humidity. OFF mode should not be set when it is possible to encounter freezing outdoor temperatures to avoid water pipe freezing.

# FAN		HVAC FAN OPERATION

Verbose Command Format: SN[address number or <blank> for global] FAN=ON or AUTO (Alternatively A can be used for Auto)

# Short Command Format: SN[address number or <blank> for global] F=ON or AUTO (Alternatively A can be used for Auto)

# Reply Format: SN[address number] F=ON or AUTO

HVAC system blowers run automatically when the heating or cooling system is operating.  They can also be turned on to run continuously to provide air movement and/or air filtration.  The Fan button on the thermostat is used to run the system blower continuously or to run automatically.  This command performs the same function as the thermostat Fan button.

# HVAC		REPORT HVAC RELAY STATES

Verbose Command Format: SN[address number or <blank> for global] HVAC?

Short Command Format: SN[address number or <blank> for global] H?

Reply Format: SN[address number] HVAC=G±Y1±W1±Y2±W2±B±O±  (see example below)

Thermostats control HVAC units by energizing various relays within the thermostat completing a circuit to the HVAC controls.  This command reports the on or off state of each relay within the thermostat.  The relay names used are consistent with HVAC terminology (Note that the compressor is active during cooling operation and during heating operation with heat pump systems):

G	Fan

Y1	First stage compressor OR Dehumidifier

W1	First stage heat (or auxiliary heat with heat pump systems) OR Humidifier

W2	Second stage heat (or 2nd stage auxiliary heat during Emergency Heat operation with heat pump systems)

Y2	Second stage compressor

O	Reversing valve cooling mode (heat pump)

B	Reversing valve heating mode (heat pump)

On (or energized) is indicated by a plus sign “+” following the relay name.  Off is indicated by a minus sign “-“ following the relay name. An example of this command sequence is as follows (commands are bold responses are shown in italics):

SN1 HVAC?	Request to the thermostat with network address 1 as to the state of the HVAC control relays

SN1 HVAC=G+Y1+W1-W2-Y2-O+B-	Model 8870 responds that the fan and first stage compressor relays are currently energized.

HIBP & LOBP		HIGH AND LOW BALANCE POINT (APPLICABLE ONLY FOR HEAT PUMPS)

Command Format: SN[address number or <blank> for global] HIBP=Integer value between 40 and 80 for °F and between 4 and 27 for °C

Reply Format: SN[address number] HIBP={value}F or C

Command Format: SN[address number or <blank> for global] LOBP=Integer value between 0 and 40 for °F and between –18 and 4 for °C

Reply Format: SN[address number] LOBP={value}F or C

Heat pumps, when operating in the heating mode, extract heat from the outdoor air and transfers it to the indoor air.  An auxiliary source of heat is usually present on heat pump systems to meet the heating demand when the heat pump can not meet the capacity needs.  At a particular outdoor temperature it is more economical to operate the auxiliary heat source than it is to operate the heat pump, this is called the Low Balance Point (LOBP).  Conversely, it is so much less economical to operate the auxiliary heat at higher outdoor temperatures that some municipalities require that the auxiliary heat be locked out above a particular temperature, this is called the High Balance Point (HIBP).  This command is used to set these temperatures. Integer values must be within the range specified for the current scale.  Model 8870 will accept this command only if the thermostat has been configured for heat pump operation and if a support module is attached to the network that has been configured for remote temperature sensing.

# Text Messaging Commands

Model 8870 incorporates two displays, a segmented display and a two-line, 16-character per line text messaging display.  These commands are used to control the text messaging display.

DATE	TEXT MESSAGING DISPLAY – DATE

Command Format: SN[address number or <blank> for global] DATE=MMDDYY {MM = 01-12, DD = 01-31, YY = 00-99}

Reply Format: SN[address number] DATE=MMDDYY

Model 8870 has a counter and can maintain a clock, once set, with reasonable accuracy over a 24 hour period.  Therefore it is necessary to send Model 8870 the current Date and Time from the automation system at least once per day.  Each variable, Date and Time, has its own command.

Date is sent in 6-digit form and will be displayed on the text messaging display as the same six digits, with each set of two separated by a “-”.  Date values with less than 6 digits, or with any of the three numbers higher than the allowable limit, will be seen as an error and the command will not be carried out.  For example the command SN1 DATE = 122304 will result in the display reading “12-23-04”.  The thermostat does recognize that there are not more than 31 days in a month, and that there are no more than 12 months, but does not recognize months with less than 31 days.  IT IS IMPORTANT TO UPDATE THE DATE VALUE AT LEAST ONCE PER DAY As Date values do not automatically increment.

If a Date value has been sent to the thermostat, it will be displayed in addition to the four Rotating Message Display messages (see PMES1-PMES4) as a fifth message.  It will be shown as the top line of the two line text messaging display.  Should there not be a Date value, only the four Rotating Message Display messages will be displayed.

# TIME	TEXT MESSAGING DISPLAY – TIME

Command Format: SN[address number or <blank> for global] TIME=HHMM (HH = 01-23, MM = 00-59)

Reply Format: SN[address number] TIME=HHMM

Model 8870 can maintain a clock, once set, with reasonable accuracy over a 24 hour period.  Therefore it is necessary to send Model 8870 the current Date and Time from the automation system at least once per day.  Each variable, Time and Date, has its own command.

Time is sent as a four digit integer with 0000 corresponding to midnight, and 2359 corresponding to 11:59 p.m. (i.e. Military time).  Noon is “1200”.  Time values with less than four digits or higher in value than 2359 will be seen as an error and the command will not be carried out.  For example the command SN1 TIME = 0631 will result in the display reading “6:31 am”.  The counter will maintain the clock to within one minute over a 24-hour period.  IT IS IMPORTANT TO UPDATE THE TIME VALUE AT LEAST ONCE PER DAY.

If a Time value has been sent to the thermostat, it will be displayed in addition to the four Rotating Message Display messages (see PMES1-PMES4) as a fifth message.  It will be shown as the bottom line of the two-line text messaging display.  Should there not be a Time value, only the four Rotating Message Display messages will be displayed.

PMES1 – PMES4	TEXT MESSAGING - ROTATING MESSAGE DISPLAY

Command Format: SN[address number or <blank> for global] PMES1 through PMES4={32 character text string}

Reply Format: SN[address number] PMES1 through PMES4={Up to 32 character text string}

Model 8870 can store and display up to four messages on a rotating basis.  The text messaging display is a two-line, 16-character display.  The first character in the top line of the display is filled with the first character in the text string of the command.  The remainder of the character spaces are filled across the top line and then down and across the bottom line.  Blanks (spaces) count as characters, and if there are not 32 characters in the message, blank spaces will be appended to the end of the message.  Each message is displayed for 5 seconds, after which the next is displayed.  If the message is filled with nothing but blank characters (spaces), then the message is skipped in the sequence.  If only one message is available, it will be permanently displayed, and if no messages (including date and time) are available none will be displayed.  The characters in the text string are limited to alphanumeric characters either upper or lower case. Leaving any one of the messages blank (i.e. no characters including spaces) results in the default message being displayed.  The default messages are:

# PMES1 	This message default is blank and is skipped in the default rotation.

PMES2

|  | C | U | R | R | E | N | T |  | S | T | A | T | U | S |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | M | O | D | E |  |  |  |  |  |  |

MODE is the current mode of operation.

# PMES3

|  | C | U | R | R | E | N | T |  | S | T | A | T | U | S |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | F | A | N |  | S | T | A | T | U | S |  |  |  |

FAN STATUS is the current fan status (ON or Auto)

# PMES4

|  | C | U | R | R | E | N | T |  | S | T | A | T | U | S |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| E | Q | U | I | P | M | E | N | T |  | S | T | A | T | U | S |

EQUIPMENT STATUS is the current state of the equipment heating, cooling, humidifier or dehumidifier outputs

TMPMES		TEXT MESSAGING – USER RESET MESSAGE

Command Format: SN[address number or <blank> for global] TMPMES={32 character text string}

Reply Format: SN[address number] TMPMES={Up to 32 character text string}

With this command messages can be shown on the text messaging display that must be acknowledged by the user at the thermostat to reset.  Examples of this type of message might be that it is time to change a filter or call for service.  The text messaging display is a two-line, 16-character display.  The first character in the top line of the display is filled with the first character in the text string of the command.  The remainder of the character spaces are filled across the top line and then down and across the bottom line.  Blanks count as characters, and if there are not 32 characters in the message, blank spaces will be appended to the end of the message.  When the thermostat receives the command, the permanent message sequence will be interrupted by the User Reset Message.  The backlight for the text messaging display will flash on for five seconds and off for two seconds ten times.  The message will also flash at a rate of 5 seconds on, 2 seconds off.  This continues until the ENTER/HOLD button on the thermostat is pressed or until a second User Reset Message is sent with no characters in the text string.  The characters in the text string are limited to alphanumeric characters either upper or lower case.

MENU		TEXT MESSAGING – USER INTERACTIVE MODE

Command Format: SN[address number or <blank> for global] MENU=ON or OFF

Reply Format: SN[address number] MENU=ON or OFF

Normally the thermostat will display the permanent messages and user reset message as described above – this is the passive display mode.  The user may want to use the text messaging display as an interactive device and this command is used for this purpose.  When ON, the permanent text message sequence is stopped and User Reset messages are ignored.  The display will show the characters designated with the MSG command.  The thermostat continues to control HVAC functions during the user interaction with the text messaging display, and as such only the Enter, Scroll Up and Scroll Down buttons may be used for interaction.

MSG		TEXT MESSAGING – USER INTERFACE MESSAGE

Command Format: SN[address number or <blank> for global] MSG={32 character text string}

Reply Format: SN[address number] MSG={Up to 32 character text string}

This command is ignored unless the text messaging display has been put in the MENU mode of operation.  When done, this command is used to enter characters to the text messaging display.  Messages are displayed continually until a new message has been received or until the thermostat is no longer in the MENU mode of operation.  The text messaging display is a two-line, 16-character display.  The first character in the top line of the display is filled with the first character in the text string of the command.  The remainder of the character spaces are filled across the top line and then down and across the bottom line.  Blanks count as characters, and if there are not 32 characters in the message, blank spaces will be appended to the end of the message.  The characters in the text string are limited to alphanumeric characters either upper or lower case.

# Keypad Lockout Commands

Use of the buttons on the thermostat can be locked out to varying degrees using the following commands.

FANLK		HVAC FAN STATE CHANGE LOCKOUT

Command Format: SN[address number or <blank> for global] FANLK=0, 1 or 2

Reply Format: SN[address number] FANLK=0, 1 or 2

There are three levels of user lockout associated with the FAN button on the thermostat.  The first, FANLK=0 represents no lockout at all.  This is the default setting.  The second, FANLK=1 allows the user to change the fan state (on or auto) for an amount of time determined by the LKTIME value (see LKTIME command section).  At the end of the time limit, the fan state will return to that which was set when the FANLK command was received.  Subsequent changes to the fan state made at the thermostat will follow the same sequence.  Finally, FANLK=2 represents a total lockout.  The fan will remain in its current state until the FANLK setting is changed.  Pressing the FAN button on the thermostat will cause the “lock” icon on the thermostat’s segmented display to light.  Releasing the button removes the icon.  This setting is stored in non-volatile memory, so on power loss the current fan lock setting will be retained.

MODELK	MODE STATE CHANGE LOCKOUT

Command Format: SN[address number or <blank> for global] MODELK=0, 1 or 2

Reply Format: SN[address number] MODELK =0, 1 or 2

There are three levels of user lockout associated with the MODE button on the thermostat.  The first, MODELK=0 represents no lockout at all.  This is the default setting.  The second, MODELK=1 allows the user to change the mode of operation (Heat, Cool, Emergency Heat, etc.) for an amount of time determined by the LKTIME value (see LKTIME command section).  At the end of the time limit, the mode of operation will return to that which was set when the MODELK command was received.  Subsequent changes to the mode of operation made at the thermostat will follow the same sequence.  Finally, MODELK=2 represents a total lockout.  The mode will remain in its current state until the MODELK setting is changed.  Pressing the MODE button on the thermostat will cause the “lock” icon on the thermostat’s segmented display to light.  Releasing the button removes the icon. This setting is stored in non-volatile memory, so on power loss the current mode lock setting will be retained.

NETLK		NETWORK OVERRIDE (HOLD) LOCKOUT

Command Format: SN[address number or <blank> for global] NETLK=0 or 1

Reply Format: SN[address number] NETLK =0 or 1

Model 8870 incorporates an ENTER button, which has three functions: user interactive thermostat set-up, User Reset Message resetting and network override.  During thermostat set-up the user interacts with the text messaging display to select various operational parameters and this button is used to enter those selections.  When the thermostat receives a User Reset Message command this button is used clear the message from the text messaging display.  During other times, this button is used to override network control of the thermostat: temperature changes, mode changes and fan state changes are controlled only by the buttons on the thermostat.  When activated, “NETWORK OVERRIDE” shows on the segmented display of the thermostat.  The NETLK command effects only the network override function.

There are two levels of user lockout associated with the HOLD or NETWORK OVERRIDE feature of the thermostat.  The first, NETLK=0 represents no lockout at all and the user is allowed to override networked operation freely (i.e. the Network Override feature is enabled).  This is the default setting.  The second, NETLK=1 represents a total lockout (i.e. the Network Override feature is disabled).  During total lockout the thermostat user is not allowed to override networked operation.  Pressing the ENTER/HOLD button on the thermostat will cause the “lock” icon on the thermostat’s segmented display to light.  Releasing the button removes the icon. This setting is stored in non-volatile memory, so on power loss the current network lock setting will be retained.

UPDNLK	TEMPERATURE CHANGE LOCKOUT

Command Format: SN[address number or <blank> for global] UPDNLK=0, 1, 2 or 3

Reply Format: SN[address number] UPDNLK=0, 1, 2 or 3

There are four levels of lockout associated with the ability to change the temperature or humidity setting at the thermostat.  The first, UPDNLK=0 represents no lockout at all.  This is the default setting.  The second, UPDNLK=1 allows the user to change the temperature setting, with no limit, for an amount of time determined by the LKTIME value (see LKTIME command section).  At the end of the time limit, the settings will return to that which was set when the UPDNLK command was received.  Subsequent changes to the temperature/humidity settings made at the thermostat will follow the same sequence.  Third, UPDNLK=2 is the same as UPDNLK=1 except the user is allowed to change the setting only by an amount specified by the LKLIMIT command.  Finally, UPDNLK=3 represents a total lockout.  The temperature/humidity settings will remain at their current value until the UPDNLK setting is changed.  Pressing the up or down button on the thermostat will cause the “lock” icon on the thermostat’s segmented display to light.  Releasing the button removes the icon. This setting is stored in non-volatile memory, so on power loss the current temperature/humidity lock setting will be retained.

LKTIME	LOCKOUT TIME LIMIT

Command Format: SN[address number or <blank> for global] LKTIME=Integer value between 0 and 255

Reply Format: SN[address number] LKTIME={set value}

Thermostat functions can be locked out to thermostat keypad changes to various levels.  One of those levels allows changes for a period of time determined by the LKTIME command.  The integer value entered represents the amount of time, in minutes, that the changed thermostat parameter  (fan, mode or temperature/humidity setting) will remain in the changed state before returning to the parameter value in place upon receipt of the lockout command.  The command will be ignored if the integer value entered is higher than the range specified.  This command has no effect unless FANLK, MODELK or UPDNLK has been set to a time limited lockout state.

LKLIMIT	LOCKOUT TEMPERATURE CHANGE LIMIT

Command Format: SN[address number or <blank> for global] LKLIMIT=Integer value between 0 and 20

Reply Format: SN[address number] LKLIMIT={set value}

Thermostat temperature/humidity settings can be locked out to thermostat keypad changes to various levels.  One of those levels allows changes within a range specified by the LKLIMIT command.  The integer value entered represents the amount of time, in minutes, that the changed thermostat parameter  (fan, mode or temperature/humidity setting) will remain in the changed state before returning to the parameter value in place upon receipt of the lockout command.  This command has no effect unless FANLK, MODELK or UPDNLK has been set to a time limited lockout state.

# Monitoring Module Commands

The Aprilaire Model 8870 thermostat does not recognize these commands, but will send out a response.  The reason a response is sent is to maintain backward compatibility with earlier product and to prevent false system communication failures due to a lack of a response.  Refer to StatNet command documentation for a description of the commands and their actions for early model Aprilaire/StatNet thermostats.

CC	MONITORING MODULE CONTACT CLOSURE STATES

Command Format: SN[address number or <blank> for global] CC?

Reply Format: SN[address number] CC=0000

This command returns the status (ON/OFF) of accessory inputs.  The Aprilaire Model 8870 thermostat will always respond that four inputs are OFF (0).  Section to be completed following specification development for the monitoring module.

CO	MONITORING MODULE CONTACT OUTPUTS

Command Format: SN[address number or <blank> for global] CO=BBBB (B = 0 for off, 1 for on or X for “don’t change”)

Reply Format: SN[address number] CO=BBBB (B = 0 for off, 1 for on)

This command sets the state (ON/OFF) of accessory outputs.  The Aprilaire Model 8870 thermostat will maintain the status of four “phantom” outputs in memory and properly respond to each command.  Section to be completed following specification development for the monitoring module.

L(1-4)	MONITORING MODULE LED INDICATORS

Command Format: SN[address number or <blank> for global] L1 through L4=ON or OFF

Reply Format: SN[address number] L1 through L4=ON or OFF

This command sets the state (ON/OFF) of accessory LED’s.  The Aprilaire Model 8870 thermostat will maintain the status of four “phantom” LED’s in memory and properly respond to each command.  Section to be completed following specification development for the monitoring module.

Auxiliary Information Commands

These commands are used to request information regarding miscellaneous thermostat parameters.

EQUIPCONFIG		THERMOSTAT HARDWARE CONFIGURATION STATUS

Command Format: SN[address number or <blank> for global] EQUIPCONFIG?

Reply Format: SN[address number] EQUIPCONFIG=wxyz; where wxyz are 0 or 1 depending on which configuration option is being represented (see text below)

Four dip switches are available on the thermostat circuit board, three to configure the thermostat for type of equipment it is to be used with and one to designate a thermostat as a “master”.  The position of these switches can be read using this command.  The response to this command will be four binary values (0 or 1) with 0 indicating the switch is off and 1 indicating the switch is on.  The first of these values (w) corresponds to servant (0 or off) or master (1 or on) designation. Thermostats designated as “master” will communicate the value of a remote sensor to which it is attached to the rest of the thermostats on the network.  With this feature a single remote sensor can be used to display information such as an outdoor temperature to all the thermostats on the network. The second (x) corresponds to electric heat source (0 or off) or fossil fuel heat source (1 or on) designation.  A qualified heating and air condition service technician should set equipment configuration switches.  The third (y) corresponds to single (0 or off) or multi-stage (1 or on) equipment configuration The fourth (z) corresponds to heat pump (0 or off) or heat/cool  (1 or on) equipment configuration.  An example of this command sequence is as follows (commands are bold responses are shown in italics):

SN1 EQUIPCONFIG?	Request to the thermostat with network address 1 as to the equipment configuration

SN1 EQUIPCONFIG = 0100	Model 8870 responds that the thermostat is configured for single stage heat pump operation with a fossil fuel heat source (i.e. dual fuel system) and is not a “master”.

BLREADY	BACKLIGHT STATUS

Command Format: SN[address number or <blank> for global] BLREADY?

Reply Format: SN[address number] BLREADY=0 (not ready) or 1 (ready)

A photosensor is integrated on the thermostat circuit board to put the display backlighting (both the segmented display and the text messaging display) in a ready state.  When ready, the first press of a button on the thermostat will light the backlighting and do nothing else.  This command is used to read whether or not the backlighting of a thermostat is in the ready state.  If the corresponding change of state command has been turned on (C12 – see Change of State command section) this information is automatically sent to the host.

BLTRIG	BACKLIGHT TRIGGER

Command Format: SN[address number or <blank> for global] BLTRIG=0 or 1; 0 is for darker, 1 is for lighter

Reply Format: SN[address number] BLTRIG=0 or 1

A photosensor is integrated on the thermostat circuit board to put the display backlighting (both the segmented display and the text messaging display) in a ready state depending on the intensity of the ambient light.  This command is used to select a relative intensity.  Setting this value to 1 means that the ambient light must be lower (room darker) for the backlight to enter a ready state while a 0 means that the ambient light must be greater (room lighter).

BLTON		TURN BACKLIGHT ON

Command Format: SN[address number or <blank> for global] BLTON

Reply Format: SN[address number] BLTON

Entering this command turns on the backlighting for both the segmented display and the text messaging display regardless of whether or not the backlight is in the “ready” state.  The backlighting stays on continually for 10 seconds and is then turned off.

ENTR		ENTER BUTTON STATUS

Reply Format: SN[address number] ENTR=0 (Pressed) or 1 (Released)

An Enter button is located below the text messaging display of the thermostat.  This button is used to enter a selection within a menu.  Automation system programmers can use the changing state of this button to integrate the text messaging display into the automation system.  This command is a status update command and is used to report when the state of the button (from inactive to pressed or from pressed to released) changes.  This command can not be used to change the state of a variable.  State change reporting is controlled by means of the corresponding change of state commands (C11 – see Change of State command section).  This command will not respond when an inquiry request is sent from the host.

SCUP & SCDN		SCROLL UP AND SCROLL DOWN BUTTON STATUS

Reply Format: SN[address number] SCUP=0 (Pressed) or 1 (Released)

Reply Format: SN[address number] SCDN=0 (Pressed) or 1 (Released)

Two buttons are located next to the text messaging display of the thermostat.  The top button is used to scroll up to various selections within a menu while the bottom button is used to scroll down.  Automation system programmers can use the changing state of these buttons to integrate the text messaging display into the automation system.  These commands are status update commands only and are used to report when the state of the button (from inactive to pressed or from pressed to released) changes.  They can not be used to change the state of a variable.  State change reporting is controlled by means of the corresponding change of state commands (C9 and C10 – see Change of State command section).  These commands will not respond when an inquiry request is sent from the host.

# Text boxes

© Research Products Corporation 2002

# SN# [Command][? or =][Value] ( Enter